PRUDENT AVOIDANCE GUIDELINES

FOR POWER FREQUENCY MAGNETIC FIELDS

K. Nuttall, Manager Network Power Quality,

ENERGEX Limited

P.J. Flanagan, Assistant General Manager Environmental Services,

Pacific Power

G. Melik, EMF Consultant,

Magshield Products International Pty. Ltd.

Radiation Protection in Australasia, vol 16, no. 3, pp. 2-12, 1999

Presented at the 23rd Annual Conference of the Australasian Radiation Protection Society Inc.

11 - 15 October, 1998, Ballarat Victoria Australia.

ABSTRACT

In March 1991, following a wide ranging inquiry into community needs and high voltage transmission line development, Sir Harry Gibbs, an ex-Chief Justice of the High Court of Australia concluded that adverse health effects from power frequency electric and magnetic fields (EMFs) had not been established.  He went on to find that there was some evidence that they might pose a risk to health.  On this basis, he recommended a policy of prudent avoidance in the construction of new transmission lines.  Since that time, a succession of inquiries in Australia and overseas have made similar findings and recommended prudent avoidance.

This paper provides practical guidance to electricity transmission and distribution utilities and other interested stakeholders in the application of prudent avoidance to the design and siting of new electrical facilities.  The paper provides background information and a range of general measures which might prudently be applied.  It is not the authors’ intention to provide precise instructions for the application of prudent avoidance but, rather, to provide a series of guiding principles which may be applied to particular situations, having regard to the specific design practices and other policies of individual electricity utilities.

# 1.	INTRODUCTION

The concept of prudent avoidance was first suggested in 1989 by Professor M. Grainger Morgan (1) as a sensible response to community concern regarding health aspects of EMF in the face of ongoing scientific uncertainty.  This uncertainty in relation to exposure to EMFs was also addressed by Sir Harry Gibbs in a wide ranging inquiry into community needs and high voltage transmission line development in Australia.  In his March, 1991 Report (2) he said:

“It has not been established that electric fields or magnetic fields of power frequency are harmful to human health but, since there is some evidence that they may do harm, a policy of prudent avoidance is recommended.”

Since 1991, a succession of major inquiries including a further two in Australia (3 and 4) have recommended prudent avoidance but the term has not been, and by its nature, cannot be defined with precision.

Prudent avoidance involves taking reasonable steps in any particular circumstance, and although a precise definition cannot be given, it is possible to provide general guidance.  The aim of this paper is to outline a range of options which may be applied in the context of prudent avoidance for transmission, distribution and beyond-the-meter situations from the consumer’s point of view.  In doing so, it is recognised that design practices and other policies of individual electricity utilities vary considerably.  Accordingly, it remains the responsibility of the designers to apply the principles appropriately to particular situations.

The paper makes no attempt to address the application of prudent avoidance in an occupational setting, either for electricity industry employees, or others exposed to magnetic fields during the course of their employment.

# 2.	PUBLIC POLICY CONSIDERATIONS

The uncertain state of the science regarding EMFs has presented significant challenges for those responsible for public policy on health and safety matters.  The Gibbs Report (2) dealt with this aspect of the EMF issue as follows:

“It then becomes a question of policy what action should be taken to avert a possible risk to public health when it cannot be said either that it is probable that the risk exists or in what circumstances a risk, if one exists, arises.  A suggestion has been made in the United States that a policy of prudent avoidance should be adopted.”

“It would not be prudent, but foolish, to make radical or expensive changes to existing lines until further scientific studies have resolved the doubts.  On the other hand, when new lines are being constructed, it may be prudent to do whatever can be done without undue inconvenience and at modest expense to avert the possible risk, remembering that if that is not done and future research establishes the existence of a real risk to health, serious problems may arise which can be remedied only at great cost.”

The recommendations contained in the Gibbs Report formed the basis of the policy subsequently adopted by many Australian electricity supply businesses.

In 1991, the Electricity Supply Association of Australia (ESAA) adopted a formal policy in relation to EMFs.  The policy recommends to ESAA members that they operate their electrical power systems prudently within Australian health guidelines, and closely monitor, and, where appropriate, sponsor high quality scientific research.

In an accompanying Advice to its members, the ESAA clarified what it meant by acting prudently in this context.  In ESAA’s view, acting prudently means embracing a range of sensible actions having regard to the uncertain state of the science, and which take into account scientific research and community concerns.  These actions are set out in the paper, and include informing employees and the public about the issue, and practising prudent avoidance (as described in the Gibbs Report) when designing and building new transmission and distribution facilities.  Such actions can include considering the design of the new facilities with respect to the EMFs which may be produced, sharing information on EMFs with the community, and taking community views into account when siting new facilities.

Since 1991, recommendations regarding prudent avoidance have been made in other jurisdictions.  In Australia, there have been two major public inquiries since Gibbs.  In 1992 in Victoria, the Peach Panel (3) recommended that:

“ Planning for all new transmission and distribution facilities take prudent avoidance into account.  When designing these facilities regard should be given to their capacity to produce magnetic fields, and in siting them, regard should be given to their proximity to houses, schools and the like.”

In 1995 following an inquiry into the interconnection of New South Wales and Queensland electricity grids with a high voltage powerline, the Australian Senate Economics References Committee (4) found that:

“In acknowledging (these) community concerns, the Committee agrees that, as a minimum policy or until evidence suggests otherwise, the concept of ‘prudent avoidance’ should continue to be practised by Government and power authorities.”

More recently in 1997, a new policy guidance booklet (5) was published by five Swedish Government authorities to help Swedish decision makers when they are required to consider the EMF health effects issue.  The advice given in the booklet is based on the precautionary principle and reflects what is known about the EMF science and the technical actions which may be possible to exercise a degree of caution given limited community resources.

The concept of prudent avoidance is considered an appropriate response while ever the current climate of scientific uncertainty persists and is as relevant now as when first recommended by Sir Harry Gibbs.  The following sections provide practical guidance to the application and implementation of prudent avoidance for electricity transmission and distribution businesses in Australia.

# 3.	PRUDENT AVOIDANCE PRINCIPLES

Internationally, there is broad consensus that a prudent approach should be taken in the design and siting of new transmission facilities.  Although there is no precise definition of prudent avoidance, there is considerable discussion in the literature which provides guidance as to how it might be applied in practice.  In particular, Sir Harry Gibbs described prudent avoidance as:

“....doing whatever can be done at modest cost and without undue inconvenience to avoid the possible risk (to health)”.....”

Although useful, this description is open to interpretation, especially in respect of the question as to what might constitute “modest cost”.  In this regard, in 1993, the California Public Utilities Commission in the United States of America published an order defining prudent avoidance as undertaking suitable activities up to 4% of the cost of a new electricity company installation project.

In a document produced by Southern California Edison Company (6) in 1994 , design guidelines were developed to:

“Implement no-cost and low-cost methods to reduce magnetic fields from new electric utility facilities.”

The application of prudent avoidance in the design and construction of new electrical facilities is a process of assessing the extent to which people may be exposed to fields produced by them and considering what “low cost” and “no cost” measures might be taken to reduce such exposure within acceptable constraints.  It is considered that the 4% limit adopted by the California Public Utilities Commission is appropriate and, accordingly it is suggested that, in the Australian context, “modest cost” or “low cost” measures should be interpreted as involving up to 4% of the total project cost.  This figure is considered reasonable and should be acceptable to many utilities.

Apart from the quantum aspect of cost considerations, it is important to consider whether the available funds should be directed towards the mitigation of electric fields, magnetic fields or both.  Because the vast majority of concerns expressed over the past 15 years have been directed towards magnetic fields, in the authors’ view, all prudent avoidance measures should be directed primarily towards magnetic fields, recognising that, in many instances, these measures will also lead to reduced electric field exposure.

In broad terms, the range of measures which may be available to reduce exposure to the fields generated by electricity utility facilities come under two broad generic headings:

1.	siting measures

2.	design measures

These measures are generally the same as those which might be applied to mitigate against magnetic interference to visual display units (VDUs), and which are listed in publication (7).

## 3.1	Siting Measures

The first aspect to be recognised in the siting of electricity utility facilities is that the process of site selection is a complex one, involving a multitude of considerations of which the possible adverse effects of EMFs is but one.  Other considerations include:

- the location of the power source and the load

- provision for future development

- the location of existing rights of way

- ease of construction and access

- cost considerations

- the nature of terrain and

- other siting constraints such as dams, residential areas, airfields, national parks, sites of particular cultural or heritage value, transport corridors and the like.

In this context, the issue of EMFs is rarely an overriding consideration but, rather, should be considered as one of several important factors.

Furthermore, because many of the factors which influence the siting of electricity utility infrastructure have a major sociological dimension, an essential part of the siting process should be the engagement of the affected community in the process.  This requires the community to be informed of the proposed project at an early stage, acquainted with the range of factors which may be relevant to the siting decisions and their genuine input sought.  In respect of EMFs, the community involvement process could include measures such as

- informing the community about the need for the line and the various site selection constraints

- providing educational material (preferably including material from independent sources on the issue of EMFs)

- providing factual information on the magnitude and extent of fields likely to be associated with the proposed facility

- providing information regarding the magnitude and extent of EMFs in the general area and in typical everyday situations, eg. in the home, the street, etc.

- seeking community input/feedback regarding siting issues.

At an early stage, the community should be informed of the consultation process to be followed and the way in which their views can be fed into it.  Following receipt of community feedback, this should be factored into site selection, along with the various other factors such as those listed above, and a decision made.

The success or otherwise of the consultative approach to site selection will be determined largely by the quality and transparency of the consultation.  In this regard, it is stressed that the utility must be prepared to listen to the concerns of individuals and communities and seek beneficial outcomes.  Experience with community consultation programs suggests that dwellings, schools, playgrounds and similar locations, especially those frequented by children, are likely to be of most interest from the perspective of EMFs.

## 3.2	Design Measures

The following design measures for reducing magnetic fields may be applied to overhead lines of all voltages:

- Increasing the (vertical) distance of the line from sensitive receptors

- Configuring the conductors to minimise the magnetic field

- Arranging the phases to minimise the magnetic field

- Using more than one conductor per phase (split phase) and arranging them to minimise the magnetic field

- Using aerial bundled conductors (up to 11,000 V)

- Reducing the current

- Shielding or active cancellation

- Locating the lines underground (in some cases this can increase the ground level magnetic field but the field strength will normally diminish more rapidly with distance).

In frequented areas, the selection of a particular pole top configuration for a new line or a rebuild should favour the configuration which results in the lowest magnetic fields, subject to cost and technical constraints.  In addition, existing conditions and future system requirements must also be considered.

The option selected should neither jeopardise the reliability nor downgrade the operating characteristics of the electricity system.  Nor should it create a hazard to maintenance personnel or to the public in general.

# 4.            PRUDENT AVOIDANCE - TRANSMISSION

The following sections describe a number of specific options for prudent avoidance which are consistent with the principles outlined in Section 3, and which may be applied to transmission facilities.

## 4.1	Transmission Lines

### 4.1.1	Distance

The most common method of reducing peoples’ exposure to EMFs is by selecting line routes (ie siting) to avoid population centres or areas where people gather.  Particular attention should be paid to schools, child care centres and other areas where children congregate.

Although a matter for developers/planning authorities, increased separation needs also to be considered when new residential development is proposed adjacent to existing transmission lines.  This could involve either the sacrificing of land within the development site or the relocation of some parts of the line.

Cost is a component of prudence, and, in considering the feasibility of alternative routes or sacrificing land with significant development potential, regard should be had to the additional cost and the principle that total expenditure on prudent avoidance not exceed 4% of the total project cost.  In cases where the “project” is a property development near an existing line, the 4% figure should be applied to the total cost of the development.

Figure 4.1, (reproduced from (7)), illustrates how magnetic field strength reduces with distance from the line.  Raising the height of the supporting structures or towers, and thus the height of the conductors, can also reduce the magnetic field strength below the line.  However, the cost and visual impact associated with the increased structure height may limit this technique to selected portions of a line.  Structure raising may be more practical for wood pole lines than for steel tower lines, due to the cost factor.

### 4.1.2	Conductor Configuration

Different arrangements of phasing can produce different magnetic field strengths for the same line current.  In general, triangular arrangements tend to provide more field cancellation than horizontal arrangements, with lower resultant field strengths.  The effect of line geometry on magnetic field profile for a typical 500 kV line is shown in Figure 4.1.

Figure 4.1   Magnetic field profile at 1 m above ground  for a typical 500 kV overhead transmission line for various conductor configurations

- Single circuit with horizontal flat configuration of phases

- Single circuit with triangular configuration of phases

- Single circuit with vertical configuration of phases

- Double circuit with vertical configuration of phases and with favourable phase sequence (acting to reduce field strength)

### Line compaction can also reduce the resultant EMFs by enhancing the field cancellation effect between the phases.  Although the ability to achieve compaction is limited by factors relating to the electrical performance of the line, it can be an attractive option as compact lines offer some other advantages.  These include reduced visual impact and reduced easement width.

### 4.1.3	Phase Arrangement

For double circuit lines, it is possible to arrange each three phase circuit with a different vertical phase arrangement in space, such that some cancellation of magnetic fields occurs.  Figure 4.2, (reproduced from (7)), illustrates this effect for a typical 500 kV transmission line, with Option 3 being the most favourable phase arrangement from the viewpoint of field reduction.  This is usually a relatively low cost option in the case of an existing line, and often a no cost option for a new line.

Selection of the proper phasing arrangement is usually the most effective way to reduce magnetic fields for two circuits on the same structure or two or more circuits on the same easement for minimal cost, if re-routing is not possible.

Figure 4.2  Magnetic field profile at 1 m above ground for a typical 500 kV double circuit transmission line with vertical conductor configuration (below)

| 1: | B | B | 2: | B | B | 3: | B | R |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | W | W |  | W | R |  | W | W |
|  | R | R |  | R | W |  | R | B |

### 4.1.4	Split Phasing

A single circuit line can be constructed as two parallel circuits with a phase arrangement designed to achieve maximum field cancellation.  This is known as the split-phase technique and may be considered if only one circuit exists on a route.  Although this form of construction is significantly more expensive than conventional single-circuit construction, it could be used for short sections of a line where it is desired to reduce fields within the suggested 4% cost limitation.

### 4.1.5	Current Reduction

A reduction in current will generally reduce magnetic field strengths.  The reduction in field strength is approximately proportional to the reduction in current.  For a given load transfer requirement, the only way to reduce the current is to increase the voltage.  However, because line voltage is generally fixed by system stability considerations, increasing line voltage will seldom be feasible within the 4% cost constraint, and other design options are likely to be preferable.

### 4.1.6	Shielding and Cancellation Loops

Shielding is the erection of a barrier between an EMF source and a subject to reduce the field strength at the subject.  A simple shielding barrier can substantially reduce electric fields from transmission lines but has little effect on magnetic fields.  Any object between the source (line) and the point of interest will provide shielding or distortion of the electric field.  Common examples are buildings, trees or any other structure.

For all practical purposes there are no means to significantly reduce or screen magnetic fields from overhead lines.  In special applications, screening of individual pieces of equipment is possible, using structures or enclosures made from special metals.

“Cancellation” or “Degaussing” loops are conducting wires suspended between adjacent structures, above or below the phase conductors to provide both shielding and cancellation effects.  They may be either “active” (energised) or “passive” (non energised) and rely on a current flow in the opposite direction to cancel or reduce the overall field produced by the line.  The use of shielding or cancellation loops is still in the research phase and, while being theoretically possible, this option is often regarded as complex, unsightly and of little practical significance.

### 4.1.7	Undergrounding

Because undergrounding is usually far more expensive than overhead construction, it does not often fall into the category of prudent avoidance, with its “minimum cost/minimum inconvenience” criteria.  There will be occasions, however, when partial undergrounding may be consistent with prudent avoidance on a total cost basis, and accordingly this option is discussed briefly below.

In underground cables, phase conductors are insulated from earth and from each other by a relatively thin layer of solid insulation, as compared to a much larger dimension of air insulation in the case of overhead lines.  Accordingly, underground phase conductors can be placed much closer together, providing a more effective field cancellation effect.

On the other hand, underground cables are normally buried 1 metre or less below ground and can be closer to people than an equivalent overhead line.  Nevertheless, due to the cancellation effect, the use of underground cables usually reduces the effective level of the magnetic field at the point of interest.  An exception to this might be the situation of cables in a street area where the point of interest is the footpath or roadway immediately above the buried cable where the field strength is still significant.

When considering undergrounding, it should be noted that, contrary to popular belief, the ground has no magnetic field shielding property and plays no part in further field reduction.

Figure 4.3, (reproduced from (7)), illustrates the difference between the magnetic field profiles of overhead transmission, distribution lines and the underground cable assuming perfect symmetry of the phase currents in all three systems.

Figure 4.3  Magnetic field profiles at 1 m above ground for typical  overhead and underground lines

- Under a 500 kV transmission line with horizontal phase configuration

- Under an 11 kV distribution line with horizontal phase configuration

- Above an underground three phase, single-core cable circuit with horizontal phase configuration and 100 mm phase separation

A three phase underground cable in one sheath will produce a lower magnetic field than the same capacity line constructed from three single-core cables because the conductors are closer together and provide more effective field cancellation than three single-core cables, especially if the latter are in flat formation.

## 4.2	Transmission Substations

The magnetic fields produced by transmission substations result largely from the outgoing and incoming overhead transmission lines, especially where they come together at entries to busbar arrangements.  Consequently, most of the prudent avoidance options available for transmission substations are those detailed in Section 4.1.  Particular opportunities may arise where multiple circuits parallel one another as they converge on the substation.  Also, there is sometimes an opportunity in the siting of the substation, or even in the fencing of the substation equipment (often part of the whole site) to minimise magnetic field strengths in areas accessible to the public.

## 4.3	Land Development

Land development adjacent to transmission lines often occurs after the transmission line has been built.  It has been suggested in some quarters that the prospect of future land subdivision and development may create an argument for utilities adopting wider easements in the first place.  This suggestion was considered by Sir Harry Gibbs in his 1991 Report.  He found no support for such a move, which would alienate additional land and increase costs to the community.  He said:

“.. it would be particularly undesirable at the present time to prescribe standards or guidelines with regard to exposure to the fields created by transmission lines or the width of easements acquired or used for such lines.”

All transmission line easements would be affected while any potential benefit would be restricted to a few isolated developments.  Furthermore, because of the variation in magnetic field strength profiles for the various design options as noted in Section 4.1, it would be impractical to attempt to prescribe easement widths which result in a consistent magnetic field outcome.  It is suggested that the application of prudent avoidance to land development should follow similar principles to those outlined for transmission line development.  In other words, it is suggested that up to 4% of the total cost of the development should be allocated to options to reduce people’s exposure to magnetic fields.  In deciding what particular prudent option to adopt, the developer may consult with the relevant utility in order to identify the most cost-effective measures available for the particular circumstance.

# 5.             PRUDENT AVOIDANCE - DISTRIBUTION

## 5.1	Distribution Lines

### 5.1.1	Siting

Due to the need to provide supply to customers, the options available to designers in siting distribution infrastructure are limited.  Distribution lines, by their very nature and function are normally located in road reserves to provide supply to customers on both sides of the road, although in some instances, they are located at the rear boundary of residential properties.

Where practicable:

- distribution lines should be located on the opposite side of the road from areas such as schools, kindergartens, child-care centres and the like

- distribution lines should be sited away from the walls of multi-storey buildings or areas where children congregate

- distribution lines should be located on the side of the road bordered by open spaces where applicable

- substations should be located at the electrical centre of their low voltage network, ie current flows in all directions should be balanced.

- As with transmission lines, the benefits of community consultation and the sharing of information should not be overlooked in the siting of distribution lines.  This is particularly relevant when high voltage overbuilds are being considered.

### 5.1.2	Design

Prudent design options which may be considered subject to their economic viability, could include:

- use of aerial bundled conductor (ABC) for low voltage reticulation to provide more effective field cancellation

- use of offset construction (ie with all phases constructed on the same side of the pole) to increase horizontal separation from the point of interest

- use of underground cable in place of overhead conductors where economically justified

- use of three phase cable instead of 3 single phase cables  (refer Section 4.1.7)

- balancing of load across all phases to reduce neutral currents

- use of insulated twisted service cable instead of open wire services to provide more effective field cancellation

- for new double circuit lines, adoption of low reactance (RWB/BWR) phasing when current flow in both circuits is in the same direction (refer Section 4.1.3)

When installing electrical facilities which involve both low voltage and high voltage, the following options apply:

- When overbuilding (or underbuilding) existing facilities, the phasing on the existing circuits should be determined and the new circuit or circuits phased to minimise the combined magnetic field strength.

- Where new or reworked subtransmission facilities are being considered on the same structure with distribution circuits, the most effective field reduction measures may be applied to the distribution circuits.

### 5.2	Distribution Substations

### 5.2.1	General Principles

Distribution and consumer substations are typically 22,000/415 V or 11,000 /415 V and are generally either pole mounted or ground mounted.  Ground mounted substations may be installed in the open, or enclosed in a pit or building.

The main sources of magnetic fields from distribution substations are the transformer windings, the high voltage and low voltage cables and line connections, the associated switchgear and also the earth straps and neutrals when forming alternative paths to earth for unbalanced currents.

Underground metallic pipes and telecommunication cables with metallic screens, or even structural steel can also be significant sources of magnetic fields if they constitute a return path for a portion of the substation earth or neutral currents (7).

The compact design of gas insulated switchgear (GIS), as compared to open or enclosed air-insulated switchgear substations, offers significantly lower magnetic fields due to a substantial reduction of the phase separation distances.  A degree of magnetic shielding is also afforded by the gas filled enclosures.

Due to the higher associated current levels, the low voltage side of a distribution substation has higher levels of magnetic field than the high voltage side.

Figure 5.1 (reproduced from (7)), shows the profiles of the magnetic field at 1 m above the substation floor from horizontally arranged busbars at 2.1 m height and 0.3 m separation.  The neutral conductor is at 0.15 m horizontal separation from the leftmost busbar.

Figure 5.1  Variation of magnetic field with distance under three phase open type LV busbars.

- Balanced current condition

- Unbalanced current condition with the net current returning via its neutral busbar

- Unbalanced current condition, but the net current returning via an alternative route.

Metal-clad substations, where mild steel is usually used for fabrication of enclosures, are afforded a modest level of shielding by the enclosure.  Also, reinforced concrete slabs, walls and floor panels can provide some magnetic field shielding.  However, it should be noted that, unless cables, busbars and the like are fully surrounded, any shielding afforded by metallic enclosures becomes less effective with increased distance from the source.  Building materials such as brick, stone, plaster, wallboards and wood have no shielding properties for magnetic fields.

The following basic magnetic field management techniques can be applied in the design of substations:

- increasing the distance of magnetic field sources from the receptor area

- reducing the conductor or busbar spacing

- selecting an appropriate phase configuration

- balancing load between phases to reduce the neutral current

Magnetic field levels in excess of about 1 microtesla  may cause interference to conventional computer monitors and the following recommendations for prudent avoidance can also serve to mitigate this effect, which is discussed in detail elsewhere (7).

### 5.2.2	Specific Measures

In designing distribution substations in situations where prudent avoidance is required, the following design measures may be considered.  Some measures are more appropriate for high rise situations, and some for outdoor substations near domestic dwellings.

In the case of high rise buildings:

- locating substations away from normally occupied areas such as offices, lunchrooms, etc.

- planning the substation layout so that the low voltage side is further away from adjacent dwellings, offices, computer rooms, etc than the HV side

- locating transformers, low voltage busbars, disconnector switches and other potentially large sources of magnetic field within the area of the substation as far away as possible from adjacent offices, etc.

- if the floor above the substation is used as residential office space, avoiding where possible, direct ceiling mounting of heavy current cables, open type busbars or disconnector switches.  The converse applies if the floor below the substation is used as office or residential space

- locating all cable trays as far as possible from the substation ceiling and walls that separate it from adjacent dwellings, offices, etc.

- designing busbars to minimise separation between phases and between phases and the neutral bus

- if practicable, orienting transformers and other sources that have uneven field patterns so that their highest field strength side is turned away from the field sensitive area

- where possible, using three phase cables in preference to three single phase cables

- using a trefoil arrangement of cables when using three single core cables in a three phase configuration.  In such cases, if the neutral conductor is a separate single core cable, placing it, where practicable, in the centre of the trefoil formation of phases

- selecting the substation equipment considering, among other important electrical parameters, its low magnetic field design, ie 11,000/415 V distribution transformers in steel housings, compact metal-clad busbars

- avoiding phase by phase grouping of single core cables in parallel circuits

- distributing all large single phase loads and all constant current load such as lighting and office equipment equally between three phases of the low voltage supply.

In the case of outdoor substations:

- positioning the low voltage side of the transformer so that barriers such as landscaping, fencing or block walls inhibit normal access to that side of the substation

- locating substations away from normally occupied areas such as bedrooms, offices, playgrounds etc.

# 6.	MISCELLANEOUS

Whilst the primary focus of this paper is on utility installations, sources within customers’ installations can also make a significant contribution to the overall magnetic field environment.  Accordingly, a brief selection of considerations relevant to customer installations are provided in the following sections.  Supply conditions may vary from utility to utility and, if inconsistencies are evident, these conditions should take precedence.

## 6.1	Commercial/Industrial Switchboards

In the case of large commercial/industrial switchboards, the busbars inside the switchboard can have an effect on field levels outside the switchboard.  The following prudent avoidance measures may be available:

- keeping the incoming line and associated meter panel and/or busbars away from frequented areas.  This will also help avoid computer interference problems.

- avoiding the use of separate conductor trays for the energised and neutral wires.  If separate trays are necessary, it is best to place them adjacent to low/no use areas.

- locating switchboards away from high use office areas if possible

- locating workstations away from switchboards when laying out new or reorganised office areas.  A distance of 4 to 5 metres is suggested to provide the additional benefit of avoiding computer VDU interference.

- using energy efficient lift motors, air conditioning equipment and industrial motors and manufacturing equipment.

## 6.2	Domestic Meters and Wiring

Generally, the principal source of magnetic fields associated with domestic meter boxes is the wires leading to the meter box.  Accordingly, prudent avoidance measures associated with meter boxes generally focus on the wiring rather than on the box itself.  The following prudent avoidance options may be available:

- in general, for new constructions, the layout of meters, switchboard and wiring may be planned in advance, giving consideration to the magnetic fields that they would produce.

- locating the meter box in an area that is not adjacent to high use areas.  Good locations would be at the garage, a closet, storage room or at the back of a wardrobe (refer Figure 6.1).  Bedroom and living room walls are better avoided to reduce fields in active use areas.  Many authorities recommend the placement of meters and  switchboard in a back-to-back arrangement, with meters outside and switchboard inside the home for security of home and occupants.  This arrangement usually places the switchboard in low-use areas (for the sake of appearance), and is consistent with prudent avoidance.

- locating the main connecting wiring away from high use areas in cases where meter location and switchboard location are separated by a significant distance, eg. where meters are installed at the fence and the switchboard is located at (or in) the house.  The connecting wiring should be run with phases and neutral grouped together, and in a ceiling space rather than a wall space, for example.

- using service wires of insulated twisted construction, as they produce significantly less fields than open wire (bare conductor) construction (refer Figure 6.1).

- minimising or avoiding situations where heavy current wiring, especially that of stoves and air-conditioning is placed in wall cavities within the house.  This type of wiring is best located and grouped together in the ceiling.  Close proximity of the phase wires and neutral helps to cancel the magnetic fields.

- in the case of two-way switches, running the neutral wire along the same path as the twin active wire connecting the two switches to provide a cancelling effect on the magnetic fields.

- using energy efficient equipment which will use less electricity and save money, as well as reducing the electrical load on the switchboard, thereby reducing magnetic fields.  Large white goods such as refrigerators, dishwashers, washing machines and dryers are often sold with energy efficient model alternatives.

Figure 6.1  Methods of reducing magnetic fields in the home

Note:

- Insulated twisted service produces 10% of the open wire service fields

- Moving the meter box 1 metre (as shown above) can reduce fields in the bedroom by 80%

## 6.3	Earth Connections

The Multiple Earthed Neutral (MEN) system is commonly used to connect a utility’s neutral at a customer’s switchboard.  This neutral is earthed at the switchboard, sometimes via a metallic earth stake, and sometimes via a metallic water pipe.  Depending on the condition of these earth connections, some fraction, or indeed, the majority of the neutral current may flow through a path other than via the utility’s neutral.  If this happens, then an earth connection or more commonly, a water pipe can become a substantial source of magnetic field.  In these situations, the supply wiring also becomes a source of significant magnetic field as the magnitudes of the active and neutral currents are not equal.

When considering options for earth connections, it is the responsibility of the owner/electrician to identify and implement appropriate actions.

If metallic water pipes are a source of magnetic fields, consideration could be given to installing a plastic joint at the entrance to the building’s water system to prevent current from adjacent earths travelling along the pipe.  In this case, the installation of a separate earth stake is mandatory for electrical safety considerations.

# 7.	CONCLUSIONS

The concept of prudent avoidance has been recommended as the most appropriate public policy response to health concerns associated with magnetic fields.  Historically it has been difficult to scope because, by its very nature it cannot be defined in precise terms.  Nevertheless, it is possible to adopt many specific measures which are consistent with the notion of doing what can be done at modest cost and without undue inconvenience to reduce people’s exposure to magnetic fields.  This paper has sought to clarify the concept of modest cost and to suggest a range of practical options or measures for transmission and distribution applications.  The paper has also touched on a number of options which may be adopted by other stakeholders in this issue such as developers, builders, electricians and home and building owners.

# 8.	ACKNOWLEDGMENTS

The authors wish to acknowledge the assistance given by many colleagues within the electricity supply industry in the development of this paper.

# 9.	REFERENCES

(1)	Grainger Morgan, M.  “Electric and Magnetic Fields from 60 Hertz Electric Power: what do we know about possible health risks?”, Department of Engineering and Public Policy, Carnegie Mellon University, Pittsburg, PA. (1989).

(2)	Gibbs, H.  “Inquiry into Community Needs and High Voltage Transmission Line Development”, NSW Govt.  (1991).

(3)	The Panel on Electromagnetic Fields and Health.  “Report to the Victorian Government”, Vict. Govt.  (1992).

(4)	Senate Economics References Committee.  “EASTLINK.  The Interconnection of NSW

and Queensland Electricity Grids with a High Voltage Powerline”,  Australian Govt.  (1995).

(5)	Swedish National Board of Occupational Safety and Health  “Low-Frequency Electrical and Magnetic Fields:  The Precautionary Principle for National Authorities - Guidance for Decision-Makers.”  Sweden: National Board of Occupational Safety and Health, National Board of Housing.  Building and Planning.  National Electrical Safety Board, National Board of Health and Welfare, and Radiation Protection Institute. (1996).

(6)	Southern California Edison “EMF Design Guidelines for New Electrical Facilities; Transmission, Substation, Distribution.”  Irwindale, Calif. SCE. (1994).

(7)	Melik, G. “Magnetic Field Mitigation to Reduce VDU Interference”, Electricity Supply Association of Australia Limited. (1996).